	AUTO EMS / MPS HEATER ERROR CODES

	Error 30   FAN_LIMP
	No fan speed signal received for 200 sec. [3min 20 sec]

	Error 31   RoLL_TERR
	Flame detected on burner after gas valve has closed

	Error 32   DATA_Err
	Malfunction or failure of NG-Lo module

	Error 35   No_SA-THM
	S/A Thermistor not detected or open circuit

	Error 36   BAdSA-THM
	S/A Thermistor not reached 33 deg within 2 min

	Error 37   TACHO-Err
	No RPM signal received or signal greater that 1500 RPM

	Error 40   OHEAT_R-A 
	Overheat of R/A klixon

	Error 41   OHEAT_S-A 
	S/A overheat switch open

	Error 42   OHEAT_THM 
	S/A Thermistor exceeded 90 deg

	Error 43   OHCooLDwn 
	Result of error 40, 41 or 42

	Error 44   RoLLOuT
	Flame sensed on Afro sensing rod

	Error 45   LOW24VOLT
	Low power supply, resulting in insufficient 24 VAC output

	Error 46   IGN_RETRY
	re-ignition attempt when burner did not light within 5 sec

	Error 50   IGN_LKOUT
	Ignition lockout after 4 ignition attempts & burner did not light

	Error 51   FLMS_LOSS
	Pilot flame loss before main burner started

	Error 52   FLM_NOGAS
	Flame detected on burner without valve being energised

	Error 53   OH_LKOUT 
	Unit had 2 over temperature conditions within 13 mins

	Error 54   RoL_LKOUT 
	Unit locked out after 3 consecutive flame roll out (3 x Err 44)

	Error 55   IGNINVALID 
	Flame lost within 10 sec of valve opening 6 consecutive times

	Error 56   PowER_UPD
	Power interruption

	Error 60   MOTOR_O-C
	Main fan motor open circuit

	Error 61   503_FAIL1 
	Malfunction or failure of NG-Lo module

	Error 62   HSI_LOCK
	HIS ignitor is open circuit

	Error 63   503_FAIL5 
	Malfunction or failure of NG-Lo module

	Error 64   503_FAIL
	Malfunction or failure of NG-Lo module

	Error 65   MTR_LKOUT
	Main fan motor open circuit and no speed sensor signal 

	Error 67   503_WD
	Malfunction or failure of NG-Lo module

	Error 68   503 nCCFG_Err 
	Malfunction or failure of NG-Lo module

	Error 69   FUSE_BLOW 
	Blown fuse or lower that 24 VAC output of transformer

	Error 70   FSAFE_LOC 
	Flame loss on backup flame sensor

	Error 71   FSaFE_LOC  
	Flame loss on backup flame sensor


