	STARPRO  HEATER ERROR CODES

	30
	Fan Limp
	No fan speed signal received for 200 sec. [3min 20 sec]

	32
	Data Error
	Board Failure

	33
	MDGU_Limp
	Feedback current not detected from Gas Valve

	35
	No_SA_THM
	S/A Thermistor not detected or open circuit

	36
	BAdSA-THM
	S/A Thermistor not reached 33 deg within 2 min

	40
	OHEAT_R-A
	Combustion fan O/H switch open

	41
	OHEAT_S-A
	S/A overheat switch open

	42
	OHEAT_THM
	S/A Thermistor exceeded 90 deg

	43
	OHCoolDwn
	Result of error 40, 41 or 42

	44
	RoLLOut
	Result of error 40, 41 or 42

	45
	LOW24VOLT
	Result of error 40, 41 or 42

	46
	IGR_NOFLM
	Flame lost at burner during ignition

	47
	IGR_BDFLM
	Flame lost during flame prove state

	48
	LOST_PRES
	Combustion Chamber Pressure switch open

	49
	LOST_FLME
	Unexpected flame loss during heating cycle

	50
	IGN_LKOUT
	No gas flue or Ignition, Afro rollout detected

	51
	RLT_NOGAS
	No gas flue or Ignition, Afro rollout detected

	52
	FLM_NOGAS
	Flame picked up, but valve not open

	53
	OH_LKOUT
	Number of O/H Cool downs events exceeded 2

	54
	RoL_LKOUT
	Duriing ignition, flame detected on Afro

	55
	IGNVALID
	After max number of ignition attempts flame not proved

	56
	PRES_STOF
	combustion fan started, but pressure switch stuck off

	57
	PRES_STON
	combustion fan off, but pressure switch stuck on

	58
	PRES_FAIL
	With combustion fan running, pressure switch has opened

	60
	MOTOR_O-C
	Motor open circuit

	61
	PUCR_STOF
	Power supplied to primary valve control relay, but relay not closing

	62
	PUCR_STON
	Primary valve control relay closed although no power app

	63
	PUCR_FAIL
	Primary valve control relay should be closed, but still open

	64
	GAS_LKOUT
	Gas valve modulating coil exceeding max of 160mA

	65
	MTR_LKOUT
	While error 30 and 60 is present, motor will lockout

	66
	SUCR_STOF
	Secondary control relay should be closed but still open

	67
	SUCR_STON
	Secondary valve control relay closed although no power app

	68
	SUCR_FAIL
	Secondary control relay should be closed but still open

	69
	FUSE_BLOW
	24 volts supply lost as fuse has blown

	70
	SS-SDNERR
	2nd micro did not shut down heating cycle

	71
	SS-STAERR
	Primary micro detected that secondary micro is calling for heat


